This master should be used by designers working on Port of Portland construction projects and by designers working for PDX tenants (“Tenants”).  Usage notes highlight a few specific editing choices, however the entire section should be evaluated and edited to fit specific project needs.

# SECTION 078100 – APPLIED FIREPROOFING

## GENERAL

DESCRIPTION

This section describes sprayed fire-resistive materials (both concealed and exposed).

REFERENCES

ASTM:  American Society for Testing and Materials

ASTM E84: Standard Test Method for Surface Burning Characteristics of Building Materials

ASTM E119: Standard Test Methods for Fire Tests of Building Construction and Materials

ASTM E136: Standard Test Method for Behavior of Materials in a Vertical Tube Furnace at 750°C

ASTM E605: Standard Test Methods for Thickness and Density of Sprayed Fire-Resistive Material (SFRM) Applied to Structural Members

ASTM E736: Standard Test Method for Cohesion/Adhesion of Sprayed Fire-Resistive Materials Applied to Structural Members

ASTM E759: Standard Test Method for Effect of Deflection on Sprayed Fire-Resistive Material Applied to Structural Members

ASTM E760: Standard Test Method for Effect of Impact on Bonding of Sprayed Fire-Resistive Material Applied to Structural Members

ASTM E761: Standard Test Method for Compressive Strength of Sprayed Fire-Resistive Material Applied to Structural Members

ASTM E859: Standard Test Method for Air Erosion of Sprayed Fire-Resistive Materials (SFRMs) Applied to Structural Members

ASTM E937: Standard Test Method for Corrosion of Steel by Sprayed Fire-Resistive Material (SFRM) Applied to Structural Members

ASTM G21: Standard Practice for Determining Resistance of Synthetic Polymeric Materials to Fungi

AWCI:  Association of the Wall and Ceiling Industry

AWCI Technical Manual 12-A: Testing and Inspection of Field Applied Sprayed Fire-Resistive Materials

CFR:  Code of Federal Regulations

40 CFR 763: Asbestos

UL:  Underwriters Laboratories, Inc.

SUBMITTALS

Submit product data for each type of product indicated.

Shop Drawings:  Submit structural framing plans indicating the following:

Locations and types of surface preparations required before applying sprayed fire-resistive material.

Extent of sprayed fire-resistive material for each construction and fire-resistance rating, including the following:

Applicable fire-resistance design designations of a qualified testing agency.

Minimum thicknesses needed to achieve required fire-resistance ratings of structural components and assemblies.

Designation of restrained and unrestrained conditions based on definitions in ASTM E119, Appendix X3 or as determined by a qualified professional engineer.

Submit product certificates for each type of sprayed fire-resistive material, signed by product manufacturer.

Submit qualification data for installer, manufacturer, professional engineer, and manufacturer’s qualified testing agency.

Submit compatibility and adhesion test reports from sprayed fire-resistive material manufacturer indicating the following:

Materials have been tested for bond with substrates.

Materials have been verified by sprayed fire-resistive material manufacturer to be compatible with substrate primers and coatings.

Interpretation of test results and written recommendations for primers and substrate preparation needed for adhesion.

Submit product test reports based on evaluation of comprehensive tests performed by a qualified testing agency, for proposed sprayed fire-resistive materials.

Submit research/evaluation reports for sprayed fire-resistive materials.

QUALITY ASSURANCE

Installer Qualifications:  Installer shall be certified, licensed, or otherwise qualified by sprayed fire-resistive material manufacturer as experienced and with sufficient trained staff to install manufacturer’s products according to specified requirements.  A manufacturer’s willingness to sell its sprayed fire-resistive materials to the Contractor or to an installer engaged by the Contractor does not in itself confer qualification on the buyer.

Installer’s responsibilities include providing professional engineering services needed to assume engineering responsibility for designation of restrained and unrestrained conditions.

Manufacturer’s Testing Agency Qualifications:  An independent testing agency, acceptable to authorities having jurisdiction, with the experience and capability to conduct the testing indicated.

Source Limitations:  Obtain sprayed fire-resistive materials through one source from a single manufacturer.

Tenants:  Delete “Port” and replace with name of tenant.

Port-Provided Testing and Inspecting Agency:  The Port will hire a testing and inspecting agency who will test for compliance with specified requirements for performance by doing the following:

Sprayed Fire-Resistive Materials Testing:

Sprayed fire-resistive materials will be randomly selected for testing from bags bearing the applicable classification marking of UL or another testing and inspecting agency acceptable to authorities having jurisdiction.  Agency will test specimens of sprayed fire-resistive materials that comply with laboratory testing requirements specified in Part 2 and are otherwise identical to installed fire-resistive materials, including application of accelerant, sealers, topcoats, tamping, troweling, rolling, and water overspray, if any of these are used in final application.

Agency will test specimens whose application the testing and inspecting agency witnessed during preparation and conditioning.  Test reports should include a description of preparation and conditioning of laboratory test specimens.

Adhesion Testing:  Test for bond per ASTM E736 and requirements in UL’s “Fire Resistance Directory” for coating materials.

Fire-Test-Response Characteristics:  Provide sprayed fire-resistive materials with the fire-test-response characteristics indicated, as determined by testing identical products per test method indicated below by UL or another qualified testing agency.  Identify bags containing sprayed fire-resistive materials with appropriate markings of applicable testing agency.

Fire-Resistance Ratings:  Indicated by design designations from UL’s “Fire Resistance Directory” or from the listings of another qualified testing agency for sprayed fire-resistive material serving as direct-applied protection tested per ASTM E119.

Surface-Burning Characteristics:  ASTM E84.

Provide products containing no detectable asbestos as determined according to the method specified in 40 CFR 763, Subpart E, Appendix E, Section 1, “Polarized Light Microscopy.”

Preinstallation Meeting:  Conduct preinstallation meeting at work site.  Review methods and procedures related to sprayed fire-resistive materials including, but not limited to, the following:

Review and finalize construction schedule and verify sequencing and coordination requirements.

DELIVERY, STORAGE, AND HANDLING

Deliver products to work site in original, unopened packages with intact and legible manufacturers’ labels identifying product and manufacturer, date of manufacture, shelf life if applicable, and fire-resistance ratings applicable to work.

Use materials with limited shelf life within period indicated.  Remove from work site and discard materials whose shelf life has expired.

Store materials inside, under cover, aboveground, and kept dry until ready for use.  Remove from work site and discard wet or deteriorated materials.

FIELD CONDITIONS

Environmental Limitations:  Do not apply sprayed fire-resistive material when ambient or substrate temperature is 40°F or lower unless temporary protection and heat is provided to maintain temperature at or above this level for 24 hours before, during, and for 24 hours after product application.

Ventilation:  Ventilate building spaces during and after application of sprayed fire-resistive material.  Use natural means or, if they are inadequate, forced-air circulation until fire-resistive material dries thoroughly.

## PRODUCTS

SPRAYED FIRE-RESISTIVE MATERIALS

General:  Provide manufacturer’s standard products complying with requirements indicated for material composition and physical properties.

Physical Properties:  Minimum values, unless otherwise indicated, or higher values required to attain designated fire-resistance ratings, measured per standard test methods referenced with each property as follows:

Sprayed fire resistive material, Type A (low density).  Sprayed fire-resistive materials consisting of factory mixed, dry formulation of gypsum or portland cement binders, mineral fibers, fillers, aggregates, and additives mixed with water at the work site with the following requirements:

Dry Density:  15 pcf, for average and individual densities, or greater if required to attain fire-resistance rating in accordance with ASTM E605 or AWCI Technical Manual 12-A, Section 5.4.5, “Displacement Method.”

Thickness:  Provide the minimum average thickness required for fire-resistance design, indicated according to the following criteria, but not less than 0.375 inch per ASTM E605:

Where the fire-resistance design lists a thickness of 1 inch or greater, the minimum allowable individual thickness of sprayed fire-resistive material shall be the design thickness minus 0.25 inch.

Where the fire-resistance design lists a thickness of less than 1 inch but more than 0.375 inch, the minimum allowable individual thickness of sprayed fire-resistive material shall be the greater of 0.375 inch or 75 percent of the design thickness.

No reduction in average thickness is permitted for fire-resistance designs where fire-resistance ratings were established at densities of less than 15 pcf.

Bond Strength:  150 lbf/sf minimum, per ASTM E736, under the following conditions:

Field test sprayed fire-resistive material that is applied to flanges of wide-flange, structural-steel members on surfaces matching those that will exist for remainder of steel receiving fire-resistive material.

If surfaces of structural steel receiving sprayed fire-resistive material are primed or otherwise painted for coating materials, perform series of bond tests specified in UL’s “Fire Resistance Directory.”  Provide bond strength indicated in the UL fire-resistance criteria, but not less than 150 lbf/sf minimum, per ASTM E736.

Minimum thickness of sprayed fire-resistive material tested in laboratory shall be 0.75 inch.

Compressive Strength:  750.24 lbf/sf, as determined in the laboratory per ASTM E761.  Minimum thickness of sprayed fire-resistive material tested shall be 0.75 inch and minimum dry density shall be as specified in the drawings, but not less than 15 pcf.

Corrosion Resistance:  No evidence of corrosion per ASTM E937.

Deflection:  No cracking, spalling, or delamination per ASTM E759.

Effect of Impact on Bonding:  No cracking, spalling, or delamination per ASTM E760.

Air Erosion:  Maximum weight loss of 0.025 g/sf in a 24-hour period, per ASTM E859.  For laboratory tests, minimum thickness of sprayed fire-resistive material shall be 0.75 inch, maximum dry density shall be 15 pcf, test specimens shall not be prepurged by mechanically induced air velocities, and tests shall be terminated after 24 hours.

Fire-Test-Response Characteristics:  Provide sprayed fire-resistive materials with the following surface-burning characteristics as determined by the testing of identical products per ASTM E84, by UL or another qualified testing and inspecting agency:

Flame-Spread Index:  10 or less.

Smoke-Developed Index:  0.

Fungal Resistance:  No observed growth on specimens per ASTM G21.

Sprayed fire resistive material, Type B (medium density).  Sprayed fire-resistive materials consisting of factory mixed, dry formulation of gypsum or portland cement binders, mineral fibers, fillers, aggregates, and additives mixed with water at the work site with the following requirements:

Dry Density:  Values for average and individual densities as required for fire-resistance ratings, per ASTM E605 or AWCI Technical Manual 12-A, Section 5.4.5, “Displacement Method,” but shall have an average density of not less than 22 pcf.

Bond Strength:  434 lbf/sf minimum, per ASTM E736.

Compressive Strength: 7,344  lbf/sf per ASTM E761.

Corrosion Resistance:  No evidence of corrosion per ASTM E937.

Deflection:  No cracking, spalling, or delamination per ASTM E759.

Effect of Impact on Bonding:  No cracking, spalling, or delamination per ASTM E760.

Air Erosion:  Maximum weight loss of 0.025 g/sf per ASTM E859.

Combustion Characteristics:  Passes ASTM E136.

Fire-Test-Response Characteristics:  Provide sprayed fire-resistive materials with the following surface-burning characteristics as determined by the testing of identical products per ASTM E84, UL, or another qualified testing and inspecting agency:

Flame-Spread Index:  10 or less.

Smoke-Developed Index:  0.

Fungal Resistance:  No observed growth on specimens per ASTM G21.

Sprayed fire resistive material, Type C (high density).  Sprayed fire-resistive materials consisting of factory mixed, dry formulation of gypsum or portland cement binders, mineral fibers, fillers, aggregates, and additives mixed with water at the work site with the following requirements:

Bond Strength:  1000 lbf/sf minimum per ASTM E736.

Compressive Strength:  43,200 lbf/sf per ASTM E761.

Dry Density:  Values for average and individual densities as required for fire-resistance ratings, per ASTM E605 or AWCI Technical Manual 12-A, Section 5.4.5, “Displacement Method,” but with an average density of not less than 39 pcf.

Corrosion Resistance:  No evidence of corrosion per ASTM E937.

Deflection:  No cracking, spalling, or delamination per ASTM E759.

Effect of Impact on Bonding:  No cracking, spalling, or delamination per ASTM E760.

Air Erosion:  Maximum weight loss of 0.025 g/sf. per ASTM E859.

Combustion Characteristics:  Passes ASTM E136.

Fire-Test-Response Characteristics:  Provide sprayed fire-resistive materials with the following surface-burning characteristics as determined by the testing of identical products per ASTM E84, UL, or another qualified testing and inspecting agency:

Flame-Spread Index:  10 or less.

Smoke-Developed Index:  0.

Fungal Resistance:  No observed growth on specimens per ASTM G21.

For exterior applications of sprayed fire-resistive material, provide formulation approved for exterior use.

AUXILIARY FIRE-RESISTIVE MATERIALS

Provide auxiliary fire-resistive materials that are compatible with sprayed fire-resistive materials and substrates and are approved by UL or another qualified testing and inspecting agency for use in fire-resistance designs indicated.

PATCHING AND REPAIR MATERIALS

Provide material for patching and repairs.  Material shall match existing or be compatible with existing fireproofing.

## EXECUTION

EXAMINATION

Examine substrates, areas, and conditions, with installer present, for compliance with requirements for substrates and other conditions affecting performance of work.  A substrate is in satisfactory condition if it complies with the following:

Substrates comply with requirements in the section where the substrate and related materials and construction are specified.

Substrates are free of oil, grease, rolling compounds, incompatible primers, loose mill scale, dirt, or other foreign substances capable of impairing bond of fire-resistive materials with substrates under conditions of normal use or fire exposure.

Objects penetrating fire-resistive material, including clips, hangers, support sleeves, and similar items, are securely attached to substrates.

Substrates are not obstructed by ducts, piping, equipment, and other suspended construction that will interfere with applying fire-resistive material.

Conduct tests according to fire-resistive material manufacturer’s written recommendations to verify that substrates are free of oil, rolling compounds, and other substances capable of interfering with bond.

Proceed with installation only after unsatisfactory conditions have been corrected.

SEQUENCING AND COORDINATION

Sequence and coordinate application of sprayed fire-resistive materials with related work specified in other sections to comply with the following requirements:

Provide temporary enclosure as required to confine spraying operations and protect the environment.

Provide temporary enclosures for applications to prevent deterioration of fire-resistive material due to exposure to weather and to unfavorable ambient conditions for humidity, temperature, and ventilation.

Avoid unnecessary exposure of fire-resistive material to abrasion and other damage likely to occur during construction operations subsequent to its application.

Do not apply fire-resistive material to metal roof deck substrates until concrete topping, if any, has been completed.  For metal roof decks without concrete topping, do not apply fire-resistive material to metal roof deck substrates until roofing has been completed; prohibit roof traffic during application and drying of fire-resistive material.

Do not apply fire resistive material to metal floor deck substrates until concrete topping has been completed.

Do not begin applying fire-resistive material until clips, hangers, supports, sleeves, and other items penetrating fire protection are in place.

Defer installing ducts, piping, and other items that would interfere with applying fire-resistive material until application of fire protection is completed.

Do not install enclosing or concealing construction until after fire-resistive material has been applied, inspected, and tested and corrections have been made to defective applications.

PREPARATION

Cover other work subject to damage from fallout or overspray of fire-resistive materials during application.

Clean substrates of substances that could impair bond of fire-resistive material, including dirt, oil, grease, release agents, rolling compounds, loose mill scale, and incompatible primers, paints, and encapsulants.

INSTALLATION

Comply with fire-resistive material manufacturer’s written instructions for mixing materials, application procedures, and types of equipment used to mix, convey, and spray on fire-resistive material, as applicable to particular conditions of installation and as required to achieve fire-resistance ratings indicated.

Apply sprayed fire-resistive material in thicknesses and densities not less than those required to achieve fire-resistance ratings designated for each condition.  Apply in greater thicknesses and densities if specified in Part 2 “Sprayed Fire-Resistive Materials” article.

Apply sprayed fire-resistive material that is identical to products tested as specified in Part 1 “Quality Assurance” article and substantiated by test reports, with respect to rate of application, accelerator use, sealers, topcoats, tamping, troweling, water overspray, or other materials and procedures affecting test results.

Extend fire-resistive material in full thickness over entire area of each substrate to be protected.  Unless otherwise recommended in writing by sprayed fire-resistive material manufacturer, install body of fire-resistive covering in a single course.

Spray apply fire-resistive materials to maximum extent possible.  Following the spraying operation in each area, complete the coverage by trowel application or other placement method recommended in writing by sprayed fire-resistive material manufacturer.

FIELD QUALITY CONTROL

Tenants:  Delete “Port” and replace with name of tenant.

Port-Provided Testing and Inspecting Agency:  The Port will hire a qualified independent testing and inspecting agency to perform field tests and inspections and to prepare test reports.

Testing and inspecting agency will interpret tests and state in each report whether tested work complies with or deviates from requirements.

Testing and Inspecting Services:  Testing and inspecting of completed applications of sprayed fire-resistive material will take place in successive stages, in areas of extent and using methods as follows.  Do not proceed with application of sprayed fire-resistive material for the next area until test results for previously completed applications of sprayed fire-resistive material show compliance with requirements.  Tested values shall equal or exceed values indicated and required for approved fire-resistance design.

Thickness for Floor, Roof, and Wall Assemblies:  For each 1000-square foot area, or partial area, on each floor, from the average of 4 measurements from a 144-square inch sample area, with sample width of not less than 6 inches per ASTM E605.

Thickness for Structural Frame Members:  From a sample of 25 percent of structural members per floor, taking 9 measurements at a single cross section for structural frame beams or girders, 7 measurements of a single cross section for joists and trusses, and 12 measurements of a single cross section for columns per ASTM E605.

Density for Floors, Roofs, Walls, and Structural Frame Members:  At frequency and from sample size indicated for determining thickness of each type of construction and structural framing member, per ASTM E605 or AWCI Technical Manual 12-A, Section 5.4.5, “Displacement Method.”

Bond Strength for Floors, Roofs, Walls, and Structural Framing Members:  For each 10,000-square foot area, or partial area, on each floor, cohesion and adhesion from one sample of size indicated for determining thickness of each type of construction and structural framing member, per ASTM E736.

If testing finds applications of sprayed fire-resistive material are not in compliance with requirements, testing and inspecting agency will perform additional random testing to determine extent of noncompliance.

Remove and replace applications of sprayed fire-resistive material where test results indicate that it does not comply with specified requirements for cohesion and adhesion, for density, or for both.

Apply additional sprayed fire-resistive material per manufacturer’s written instructions where test results indicate that thickness does not comply with specified requirements.

Additional testing and inspecting, at Contractor’s expense, may be performed to determine compliance of replaced or additional work with specified requirements.

CLEANING, PROTECTING, AND REPAIR

Cleaning:  Immediately after completing spraying operations in each containable area of work, remove material overspray and fallout from surfaces of other construction and clean exposed surfaces to remove evidence of soiling.

Protect sprayed fire-resistive material, according to advice of product manufacturer and installer, from damage resulting from construction operations or other causes so fire protection will be without damage or deterioration at time of substantial completion.

Coordinate application of sprayed fire-resistive material with other construction to minimize need to cut or remove fire protection.  As installation of other construction proceeds, inspect sprayed fire-resistive material and patch any damaged or removed areas.

Repair or replace work that has not been successfully protected.

END OF SECTION 078100