This master should be used by designers working on Port of Portland construction projects and by designers working for PDX tenants (“Tenants”).  Usage notes highlight a few specific editing choices, however the entire section should be evaluated and edited to fit specific project needs.

SECTION 220590 – PRESSURE TESTING OF PLUMBING SYSTEMS

GENERAL

DESCRIPTION

This section describes pressure testing of plumbing piping systems.

REFERENCES

UPC:  Uniform Plumbing Code

SUBMITTALS

Submit the following:

Test plan and schedule:  For testing of piping and ductwork systems.

Test Reports:

Certificate of completion, inspection, and test by authority having jurisdiction on required piping systems.

Certificate of test approval by the Port on all systems.

The Port will record tests that it witnesses.

Use only if Commissioning Section 019100 is included in the project manual.

Coordinate with commissioning plan and schedule.

QUALITY ASSURANCE

Code Compliance:  Perform required tests in the presence of the authority having jurisdiction.

Port Witness:  Perform all tests in the presence of the Port.

Simultaneous Testing:  Test observations by the authority having jurisdiction and the Port need not occur simultaneously.

PRODUCTS

Not Used.

EXECUTION

GENERAL

Piping:  Test prior to concealment, insulation being applied, and connection to equipment, fixtures, or specialties.  Conduct tests with all valves 10 percent closed except for  those used to isolate the test section.

Leaks:  Repair all leaks and retest until stipulated results are achieved.

Notification:  Advise the Port 48 hours in advance of each test.  Failure to so notify will require test to be rescheduled.

Testing Equipment:  Provide all necessary pumps, gauges, connections and similar items required to perform the tests.

TESTING REQUIREMENTS

Sanitary and Roof Drainage Systems:  Test entire system or sections of system by closing all openings in piping except highest opening and filling system with water to point of overflow.  If system is tested in sections, plug each opening except highest opening of section under test and fill each section with water, but none with less than 10-feet head of water.  Keep water in system, or in portions under test, for at least 45 minutes before inspection starts.  Test for two hours with no drop allowed.  Locate and repair leaks.

Domestic Water Systems:  Test in accordance with UPC.

Piping:  Test all piping as noted below, with no leaks or loss in pressure for time indicated.  Repair or replace defective piping until tests are completed successfully.

Confirm test pressure before proceeding with the work.

| System | Test Pressure | Test Medium | Test Duration |
| --- | --- | --- | --- |
| Natural gas | 150 psig | Air | 4 hours |
| Non-potable water | 150 psig | Water | 4 hours |

Vacuum Waste System:  See Section 221320, Vacuum Grease Waste Removal System, for vacuum system testing requirements.

END OF SECTION 220590