This master should be used by designers working on Port of Portland construction projects and by designers working for PDX tenants (“Tenants”).  Usage notes highlight a few specific editing choices, however the entire section should be evaluated and edited to fit specific project needs.

# SECTION 280513 – CONDUCTORS AND CABLES FOR ELECTRONIC SAFETY AND SECURITY

## GENERAL

DESCRIPTION

This section describes:

Coaxial cabling.

RS-232 cabling.

RS-485 cabling.

Low-voltage control cabling.

Control-circuit conductors.

Fire alarm wire and cable.

RELATED WORK SPECIFIED ELSEWHERE

Section 078400, Firestopping

Section 260526, Grounding and Bonding for Electrical Systems

Section 260533, Raceway and Boxes for Electrical Systems

Section 260536, Cable Trays for Electrical Systems

Section 260543, Underground Ducts and Raceways for Electrical Systems

Section 260553, Identification for Electrical Systems

Section 281300, Security Access Control System

Section 282300, Video Surveillance

REFERENCES

BICSI:  Building Industry Consulting Service International

BICSI ITSIM Ch. 4: Pulling Cable

BICSI ITSIM Ch. 6: Cable Termination Practices

NECA:  National Electrical Contractors Association

NECA 1: Standard Practice of Good Workmanship in Electrical Construction

NEMA:  National Electrical Manufacturers Association

NEMA 250: Enclosures for Electrical Equipment (1000 Volts Max)

NFPA:  National Fire Protection Association

NFPA 70: National Electric Code

NFPA 72: National Fire Alarm and Signaling Code

NFPA 262: Standard Method of Test for Flame Travel and Smoke of Wires and Cables for Use in Air-Handling Spaces

TIA:  Telecommunications Industry Association

TIA 568-B.1:  Minimum 4-Pair Sc-TP Patch Cable Bend Radius

UL:  Underwriters Laboratories:

UL 83: Thermoplastic-Insulated Wires and Cables

UL 1581: Reference Standard for Electrical Wires, Cables, and Flexible Cords

UL 1655: Standard for Community-Antenna Television Cables

UL 1666: Standard for Test for Flame Propagation Height of Electrical and Optical-Fiber Cables Installed Vertically in Shafts

SUBMITTALS

Submit the following materials:

Product Data:  Submit for each type of product indicated.

For coaxial cable, submit the following installation data for each type used:

Nominal OD.

Minimum bending radius.

Maximum pulling tension.

Qualification Data:  For qualified layout technician, installation supervisor, and field inspector.

Maintenance Data:  For wire and cable to include in maintenance manuals.

Cable test data per testing requirements of Part 3.

PROJECT CONDITIONS

Environmental Limitations:  Do not deliver or install cables and connecting materials until wet work in spaces is complete and dry, and temporary HVAC system is operating and maintaining ambient temperature and humidity conditions at occupancy levels during the remainder of the construction period.

## PRODUCTS

MANUFACTURERS

Acceptable manufacturers:

Belden CDT Inc., Electronics Division.

West Penn Wire/CDT, a division of Cable Design Technologies.

Or equal.

COAXIAL CABLE

General Coaxial Cable Requirements:  Broadband type, recommended by cable manufacturer specifically for broadband data transmission applications.  Coaxial cable and accessories shall have 75-ohm nominal impedance with a return loss of 20 dB maximum from 7 to 806 MHz.

RG-11/U:  NFPA 70, Type CATV.

No. 14 AWG, solid, copper-covered steel conductor.

Gas-injected, foam-PE insulation.

Double shielded with 100 percent aluminum polyester tape and 60 percent aluminum braid.

Jacketed with sunlight-resistant, black PVC or PE.

Suitable for outdoor installations in ambient temperatures ranging from minus 40 to plus 85°C.

RG59/U:  NFPA 70, Type CATVR.

No. 20 AWG, solid, silver-plated, copper-covered steel conductor.

Gas-injected, foam-PE insulation.

Triple shielded with 100 percent aluminum polyester tape and 95 percent aluminum braid; covered by aluminum foil with grounding strip.

Color-coded PVC jacket.

RG-6/U:  NFPA 70, Type CATV or CM.

No. 16 AWG, solid, copper-covered steel conductor; gas-injected, foam-PE insulation.

Double shielded with 100 percent aluminum-foil shield and 60 percent aluminum braid.

Jacketed with black PVC or PE.

Suitable for indoor installations.

RG59/U:  NFPA 70, Type CATV.

No. 20 AWG, solid, copper-covered steel conductor; gas-injected, foam-PE insulation.

Double shielded with 100 percent aluminum polyester tape and 40 percent aluminum braid.

PVC jacket.

RG59/U (Plenum Rated):  NFPA 70, Type CMP.

No. 20 AWG, solid, copper-covered steel conductor; foam fluorinated ethylene propylene insulation.

Double shielded with 100 percent aluminum-foil shield and 65 percent aluminum braid.

Copolymer jacket.

NFPA and UL compliance, listed and labeled by an NRTL acceptable to authorities having jurisdiction as complying with UL 1655, and with NFPA 70 “Radio and Television Equipment” and “Community Antenna Television and Radio Distribution” Articles.  Types are as follows:

CATV Cable:  Type CATV.

CATV Plenum Rated:  Type CATVP, complying with NFPA 262.

CATV Riser Rated:  Type CATVR, complying with UL 1666.

CATV Limited Rating: Type CATVX.

COAXIAL CABLE HARDWARE

Coaxial-Cable Connectors:  Type BNC, 75 ohms.

RS-232 CABLE

Standard Cable:  NFPA 70, Type CM.

Paired, 2 pairs, No. 22 AWG, stranded (7x30) tinned copper conductors.

Polypropylene insulation.

Individual aluminum foil-polyester tape shielded pairs with 100 percent shield coverage.

PVC jacket.

Pairs are cabled on common axis with No. 24 AWG, stranded (7x32) tinned copper drain wire.

Flame Resistance:  Comply with UL 1581.

Plenum-Rated Cable:  NFPA 70, Type CMP.

Paired, 2 pairs, No. 22 AWG, stranded (7x30) tinned copper conductors.

Plastic insulation.

Individual aluminum foil-polyester tape shielded pairs with 100 percent shield coverage.

Plastic jacket.

Pairs are cabled on common axis with No. 24 AWG, stranded (7x32) tinned copper drain wire.

Flame Resistance:  Comply with NFPA 262.

RS-485 CABLE

Standard Cable:  NFPA 70, Type CM.

Paired, 2 pairs, twisted, No. 22 AWG, stranded (7x30) tinned copper conductors.

PVC insulation.

Unshielded.

PVC jacket.

Flame Resistance:  Comply with UL 1581.

Plenum-Rated Cable:  NFPA 70, Type CMP.

Paired, 2 pairs, No. 22 AWG, stranded (7x30) tinned copper conductors.

Fluorinated ethylene propylene insulation.

Unshielded.

Fluorinated ethylene propylene jacket.

Flame Resistance:  NFPA 262, Flame Test.

Retain one or more of four paragraphs in this article; difference in paragraphs is the conductor size and insulation type.  Other conductor sizes and insulation types are available.

LOW-VOLTAGE CONTROL CABLE

Paired Cable:  NFPA 70, Type CMG.

1 pair, twisted, No. 16 AWG, stranded (19x29) tinned copper conductors.

PVC insulation.

Unshielded.

PVC jacket.

Flame Resistance:  Comply with UL 1581.

Plenum-Rated, Paired Cable:  NFPA 70, Type CMP.

1 pair, twisted, No. 16 AWG, stranded (19x29) tinned copper conductors.

PVC insulation.

Unshielded.

PVC jacket.

Flame Resistance:  Comply with NFPA 262.

Paired Cable:  NFPA 70, Type CMG.

1 pair, twisted, No. 18 AWG, stranded (19x30) tinned copper conductors.

PVC insulation.

Unshielded.

PVC jacket.

Flame Resistance:  Comply with UL 1581.

Plenum-Rated, Paired Cable:  NFPA 70, Type CMP.

1 pair, twisted, No. 18 AWG, stranded (19x30) tinned copper conductors.

Fluorinated ethylene propylene insulation.

Unshielded.

Plastic jacket.

Flame Resistance:  NFPA 262, Flame Test.

CONTROL-CIRCUIT CONDUCTORS

Class 1 Control Circuits:  Stranded copper, Type THHN-THWN, in raceway complying with UL 83.

Class 2 Control Circuits:  Stranded copper, Type THHN-THWN, in raceway complying with UL 83.

Class 3 Remote-Control and Signal Circuits:  Stranded copper, Type TW or TF, complying with UL 83.

FIRE ALARM WIRE AND CABLE

General Wire and Cable Requirements:  NRTL listed and labeled as complying with NFPA 70, Article 760.

Initiating Device Circuits:  Twisted, unshielded pair, No. 16 AWG size as recommended by system manufacturer.

Speaker Circuits:  Twisted, shielded pair, No. 14 AWG size as recommended by system manufacturer.

Strobe Circuits:  No. 12 AWG THHN, red indicating positive and black indicating negative.

Non-Power-Limited Circuits:  Solid-copper conductors with 600-V rated, 75 C, color-coded insulation.

Low-Voltage Circuits:  No. 14 AWG, minimum.

Line-Voltage Circuits:  No. 12 AWG, minimum.

## EXECUTION

INSTALLATION OF CONDUCTORS AND CABLES

Comply with NECA 1.

General Requirements for Cabling:

Comply with TIA-568-B.1.

Comply with BICSI ITSIM, Ch. 6, “Cable Termination Practices.”

Terminate all conductors; no cable shall contain unterminated elements.  Make terminations only at indicated terminals.

Cables may not be spliced.  Secure and support cables at intervals not exceeding 30 inches and not more than 6 inches from cabinets, boxes, fittings, outlets, racks, frames, and terminals.

Bundle, lace, and train conductors to terminal points without exceeding manufacturer’s limitations on bending radii, but not less than radii specified in BICSI ITSIM, “Cabling Termination Practices” Chapter.  Install lacing bars and distribution spools.

Do not install bruised, kinked, scored, deformed, or abraded cable.  Remove and discard cable if damaged during installation and replace it with new cable.

Cold-Weather Installation:  Bring cable to room temperature before dereeling.  Heat lamps shall not be used for heating.

Pulling Cable:  Comply with BICSI ITSIM, Ch. 4, “Pulling Cable.”  Monitor cable pull tensions.

Pulling wire and cable into conduit or trays shall be completed without damaging or putting undue stress on the cable insulation.  UL listed pulling compounds are acceptable lubricants for pulling wire and cable.  Grease is not acceptable.  Raceway construction shall be complete, cleaned, and protected from the weather before cable is placed.

Outdoor Coaxial Cable Installation:

Install outdoor connections in enclosures complying with NEMA 250, Type 4X.  Install corrosion-resistant connectors with properly designed O-rings to keep out moisture.

Attach antenna lead-in cable to support structure at intervals not exceeding 36 inches.

Separation from EMI Sources:

Separation between cables in nonmetallic raceways and unshielded power conductors and electrical equipment shall be as follows:

Electrical Equipment Rating Less Than 2 kVA:  A minimum of 5 inches.

Electrical Equipment Rating between 2 and 5 kVA:  A minimum of 12 inches.

Electrical Equipment Rating More Than 5 kVA:  A minimum of 24 inches.

Separation between communications cables in grounded metallic raceways and unshielded power lines or electrical equipment shall be as follows:

Electrical Equipment Rating Less Than 2 kVA:  A minimum of 2-1/2 inches.

Electrical Equipment Rating between 2 and 5 kVA:  A minimum of 6 inches.

Electrical Equipment Rating More Than 5 kVA:  A minimum of 12 inches.

Separation between communications cables in grounded metallic raceways and power lines and electrical equipment located in grounded metallic conduits or enclosures shall be as follows:

Electrical Equipment Rating Less Than 2 kVA:  No requirement.

Electrical Equipment Rating between 2 and 5 kVA:  A minimum of 3 inches.

Electrical Equipment Rating More Than 5 kVA:  A minimum of 6 inches.

Separation between Cables and Electrical Motors and Transformers, 5 kVA or HP and Larger:  A minimum of 48 inches.

Separation between Cables and Fluorescent Fixtures:  A minimum of 5 inches.

FIRE ALARM WIRING INSTALLATION

Comply with NECA 1 and NFPA 72.

Wiring Method:  Install wiring in metal raceway according to Section 260533, Raceway and Boxes for Electrical Systems.

Install plenum cable in environmental air spaces, including plenum ceilings.

Fire alarm circuits and equipment control wiring associated with the fire alarm system shall be installed in a dedicated raceway system.  This system shall not be used for any other wire or cable.

Wiring within Enclosures:  Separate power-limited and non-power-limited conductors as recommended by manufacturer.  Install conductors parallel with or at right angles to sides and back of the enclosure.  Bundle, lace, and train conductors to terminal points with no excess.  Connect conductors that are terminated, spliced, or interrupted in any enclosure associated with the fire alarm system to terminal blocks.  Mark each terminal according to the system’s wiring diagrams.  Make all connections with approved crimp-on terminal spade lugs, pressure-type terminal blocks, or plug connectors.

Color-Coding:  Color-code fire alarm conductors differently from the normal building power wiring.  Use one color-code for alarm circuit wiring and another for supervisory circuits.  Color-code audible alarm-indicating circuits differently from alarm-initiating circuits.  Use different colors for visible alarm-indicating devices.  Paint fire alarm system junction boxes and covers red.

CONTROL-CIRCUIT CONDUCTORS

Minimum Conductor Sizes:

Class 1 remote-control and signal circuits, No. 14 AWG.

Class 2 low-energy, remote-control and signal circuits, No. 16 AWG.

Class 3 low-energy, remote-control, alarm and signal circuits, No. 12 AWG.

CONNECTIONS

Comply with requirements in Section 281300, Security Access Control System for connecting, terminating, and identifying wires and cables.

Comply with requirements in Section 282300, Video Surveillance for connecting, terminating, and identifying wires and cables.

Comply with requirements in Section 283100, Fire Detection and Alarm for connecting, terminating, and identifying wires and cables.

POWDER-ACTUATED FASTENERS

Powder-actuated fasteners are not allowed.

FIRESTOPPING

Comply with requirements in Section 078400, Penetration Firestopping.

GROUNDING

For low-voltage wiring and cabling, comply with requirements in Section 260526, Grounding and Bonding for Electrical Systems.

IDENTIFICATION

Comply with requirements for identification specified in Section 260553, Identification for Electrical Systems.

FIELD QUALITY CONTROL

Perform tests and inspections.

Visually inspect cable jacket materials for UL or third-party certification markings.  Inspect cabling terminations to confirm color-coding.

Visually inspect cable placement, cable termination, grounding and bonding, equipment, and labeling of all components.

Test cabling for DC loop resistance, shorts, opens, intermittent faults, and polarity between conductors.  Test operation of shorting bars in connection blocks.  Test cables after termination.

Instruments used for continuity measurements shall have a resolution of 0.1 ohms and an accuracy of better than 0.1 percent of reading plus 0.3 ohms.  A 500-volt megohmmeter shall be used for insulation resistance measurements.

Coaxial Cable Tests:  Comply with requirements of TIA testing practices and procedures.

Document data for each measurement.  Print data for submittals in a summary report that is formatted using Table 10.1 in BICSI TDMM as a guide, or transfer the data from the instrument to the computer, save as text files, print, and submit.

End-to-end cabling will be considered defective if it does not pass tests and inspections.

Prepare test and inspection reports.

EXISTING CIRCUITS

Confirm the destination and purpose of each existing circuit before connecting to new equipment and new wiring.  Connections shown on the one-line diagram drawing are the preferred connections.  In any cases where drawings conflict, the conflict will be resolved by the Port.

Remove existing terminations with as much existing cable as possible.  Existing cable length may require different routings within manhole vaults than are shown on the drawings.  Do not unnecessarily cut off any existing cable length.

END OF SECTION 280513