This master should be used by designers working on Port of Portland construction projects and by designers working for PDX tenants (“Tenants”).  Usage notes highlight a few specific editing choices, however the entire section should be evaluated and edited to fit specific project needs.

- SECTION 232100 – UNDERGROUND HYDRONIC PIPING

- GENERAL

      - DESCRIPTION

        - This section describes direct buried prefabricated piping systems for heating hot water, condenser water, and chilled water.

      - RELATED WORK SPECIFIED ELSEWHERE

        - Section 015713, Temporary Erosion, Sediment, and Pollution Control

        - Section 230500, Common Work Results for HVAC

        - Section 230518, Expansion Compensation

        - Section 230529, Hangers and Supports for HVAC Piping and Equipment

        - Section 230553, Identification for HVAC Piping and Equipment

        - Section 230590, Pressure Testing of HVAC Systems

        - Section 230719, HVAC Insulation

        - Section 232000, HVAC Piping

        - Section 232500, HVAC Water Treatment

        - Section 312300, Trenching, Backfilling, and Compacting

        - Section 312319, Dewatering

      - REFERENCES

        - ASTM:  American Society for Testing and Materials

          - ASTM C591: Standard Specification for Unfaced Preformed Rigid Cellular Polyisocyanurate Thermal Insulation

          - ASTM D1248: Standard Specification for Polyethylene Plastics Extrusion Materials for Wire and Cable

      - SUBMITTALS

        - Product Data:  Submit product data for products specified herein.

        - Installation Manuals:  Submit installation manuals for prefabricated piping systems.

        - Shop Drawings:  Submit complete shop drawings for piping systems including elbows, tees, flanges, coupling locations, coupling types, and anchors.  Include cutting lengths and thrust block sizes.

        - Factory Test Reports:  Submit factory test report for each concealed weld location.  Identify each section of piping with a unique number to allow for easy comparison with test report.

        - Field Piping Tests:  Submit report on field piping tests with signatures of the Port and manufacturer’s representative witnessing.

      - QUALITY ASSURANCE

        - The Contractor shall engage the services of a qualified manufacturer’s representative to provide instruction on installation procedures for manufacturer’s piping and to be present on site to assist during critical stages of installation and testing.

        - Include a report consisting of the installation log indicating actual installed conditions and test certification signed by the manufacturer’s representative above, the Contractor, and the Port.  Include certification by manufacturer’s representative that the installation is in accordance with the manufacturer’s recommendations.

- PRODUCTS

      - LARGE DIAMETER PREFABRICATED WATER PIPING – DOUBLE WALL

        - Acceptable Manufacturers:  Rovanco, Thermal Pipe, or pre-bid approved equal.

        - Service:

          - Buried chilled water.

          - Buried heating water.

          - Buried condenser water.

        - General:  Provide complete prefabricated underground water piping system suitable for direct burial as indicated on the drawings and with the following characteristics:

| Nominal Pipe Size in inches | Minimum Insulation Thickness in inches | Nominal Jacket Size in inches | Jacket Thickness in Mils |
| --- | --- | --- | --- |
| 2" | 1.91" | 6" | 200 |
| 3" | 1.35" | 6" | 200 |
| 4" | 1.57" | 8" | 175 |
| 6" | 1.51" | 10" | 175 |
| 8" | 1.72" | 12" | 175 |
| 10" | 1.48" | 14" | 175 |
| 12" | 1.38" | 16" | 175 |
| 14" | 1.74" | 18" | 175 |
| 16" | 1.70" | 20" | 200 |
| 18" | 1.89" | 22" | 200 |
| 20" | 1.86" | 24" | 225 |

        - Service Piping:

          - HDPE Pipe:  Polyethylene resin compound in accordance with ASTM P3350. All service piping shall have a pressure rating of 160 psi. Provide butt fusion or electro-fusion socket weld joints on pipe and fittings.  Provide straight sections in 40-foot lengths with piping exposed at each end for field joint fabrication.

          - Steel Pipe:  Schedule 40 or 80 A-53 Grade-B black steel pipe and fittings for pipe sizes up to 8 inches.  Standard weight 0.375-inch wall or heavy weight 0.5-inch wall for piping 10 inches and larger.  Provide long radius pipe elbows.  Provide butt weld joints on pipe and fittings

        - Jacketing:

          - Integral sealed unit consisting of Type III, Grade P34, Class C Category 5 high density polyethylene plastic carrier pipe.

          - Open ends of pipe and fittings shall have manufacturer’s end seals compatible with the jacketing.  Field cuts shall have a manufacturer’s standard seal system for field sealing of pipes.

        - Insulation:

          - Provide rigid, 90 to 95 percent closed cell polyurethane with a 1.9 to 2.1 pound per cubic foot density and an aged coefficient of thermal conductivity (K) of 0.165 BTU/(HR*F/IN.) at 73ºF.

          - Install insulation on all pipe and fittings, completely filling the void between the pipe and jacket.

          - Where support guides are shown on drawings, they shall be factory installed, to assure equal thickness of insulation around the pipe.

        - Field joints:

          - Where electro-fusion socket weld joints are used, provide larger diameter jacket to obtain listed insulation thickness over the joint as needed.

        - Accessories:  Provide all required accessories including anchor plates, wall sleeves, and miscellaneous materials as required for attachment to steel pipe at ends and as required and detailed to a complete installation.

      - PREFABRICATED PEX RADIANT PIPING

        - Acceptable Manufactures:  Rovanco Rhinoflex, or equal.

        - Service:  Direct buried radiant distribution piping.

        - General:  Provide complete factory prefabricated HDPE jacketed, insulated, two water pipe system with all necessary fittings, seals, and accessors for direct burial.

        - Expansion:

          - Components of carrier pipe, insulation, and jacket shall be able to expand and contract as a unit without overstressing or adversely affecting the materials.

          - Coordinate with the piping system supplier to ensure proper design of the piping system expansion and construction.

        - Service Pipe:

          - Provide two pipes for supply and return.

          - Cross-linked PEX piping, SDR-11, 100-psi working pressure up to 180F working temperature.

          - High density polyethylene, 160-psi working pressure up to 110F working temperature.

        - Insulation:  Polyurethane closed cell insulation with K-Factor of 0.149.  Fill void between dual pipes and outer jacket completely.

        - Jacket:  Outer protective jacket corrugated seamless polyethylene completely encompassing and protecting the insulation from moisture and damage, designed for H-20 loading at a burial depth of 2-foot minimum.

        - Joints:

          - Straight run joints field-insulated in accordance with the manufacturer’s instructions, using polyurethane foam poured in an HDPE sleeve and sealed with a heat shrink sleeve.

          - Joint closures and insulation occur at straight sections of pipe.

          - Insulation and jacketing materials furnished by piping system supplier.

        - Fittings:  Standard component factory prefabricated and pre-insulated to the thickness specified.

        - Accessories:  Provide required accessories including wall sleeves and miscellaneous materials as required for attachment to steel or copper pipe at ends and as required for a complete installation.

- EXECUTION

      - PREPARATION

        - Measurements, Lines and Levels:

          - Check dimension at the building site and establish lines and levels for the work specified in this section.

          - Establish all inverts, slopes and manhole elevations by instrument, working from an established datum point.  Provide elevation markers for use in determining slopes and elevations.

          - Use established grid and area lines for locating trenches in relation to building and boundaries.

      - PIPING JOINTS

        - Join prefabricated water piping as specified herein and in accordance with manufacturer’s recommendations.

      - ADJUSTING AND CLEANING

        - Adjust and clean according to Section 232000, HVAC Piping and Section 232500, HVAC Water Treatment.

      - PREFABRICATED PIPE INSTALLATION

        - Install all piping as to vent and drain to building.

        - Utility Marking:  Install utility warning tape and location wire over the entire length of the underground piping utilities in accordance with requirements of Section 312300, Trenching, Backfilling, and Compacting.

        - Field welds at conduit closures shall be tested for leaks.  Pressurize with compressed air at 5 psig.  Check with soap suds.

        - Install anchors within 5 feet of each end of prefabricated piping.  Concrete shall be cast over the anchorplate and conduit and shall be large enough for firm anchorage into undisturbed soil.  Concrete block shall be a minimum 30 inches in length and shall extend at least 9 inches above and below prefabricated piping.

      - TESTING

        - Test carrier and service piping according to requirements of Section 230590, Pressure Testing of HVAC Systems, and in accordance with the manufacturer’s recommendations.

END OF SECTION 232100