U.S. DEPARTMENT OF TRANSPORTATION
FEDERAL AVIATION ADMINISTRATION

NORTHWEST MOUNTAIN REGION

AIRPORT IMPROVEMENT PROGRAM

MODIFICATION OF AIRPORT DESIGN STANDARDS

AGIS INPUT FORM

| # BACKGROUND |  |  |  |
| --- | --- | --- | --- |
| AIRPORT: | LOCATION (CITY/STATE): |  | LOC ID: |
| EFFECTED RUNWAY/TAXIWAY: | 5. APPROACH (EACH RUNWAY): PIR NPI VISUAL | 6. AIRPORT REF. CODE (ARC): |  |
| 7. DESIGN AIRCRAFT (EACH RUNWAY/TAXIWAY): |  |  |  |
| AIP GRANT NUMBER: PFC NUMBER: |  |  |  |
| # MODIFICATION OF STANDARDS |  |  |  |
| TITLE OF STANDARD BEING MODIFIED (CITE REFERENCE DOCUMENT): AC NUMBER: 150/5370-10H CHAPTER: D-751 PARAGRAPH: 2.7 PAGE NUMBER: |  |  |  |
| 1. STANDARD/REQUIREMENT: 751-2.7 Steps. The steps or ladder bars shall be gray or malleable cast iron or galvanized steel. The steps shall be the size, length, and shape shown on the plans and those steps that are not galvanized shall be given a coat of asphalt paint, when directed. |  |  |  |
| 2. PROPOSED: Replace this section as follows: 751-2.7 Steps. The steps shall be reinforced polypropylene plastic conforming to the requirements of ASTM C 478 and ASTM C 497, except that the minimum horizontal pullout load shall be 1,500 pounds. The steel shall be Grade 60, 1/2 inch (13 mm) deformed reinforcing bar conforming to ASTM A 615. The polypropylene shall conform to ASTM D 4101. The entire polypropylene material surrounding the reinforced steel bar shall be encased monolithically with a minimum thickness over the steel of 1/16 inch (1.6 mm). Steps or ladder bars made of gray or malleable cast iron are acceptable alternatives. The steps shall be the size, length, and shape shown on the plans and those steps that are not galvanized shall be given a coat of bituminous paint, when directed. |  |  |  |
| 3. EXPLAIN WHY STANDARD CANNOT BE MET (FAA ORDER 5300.1E): AC 150 5300-13A states that the design of storm drainage systems must meet local requirements and address storm water quality issues in accordance with state and local permits. The Port of Portland is a co-permittee with the City of Portland on Municipal Separate Storm Sewer System (MS4) Permit No. 101314, which was issued by the Oregon Department of Environmental Quality (DEQ) in 2011. This permit requires the Port to monitor levels of metals dissolved within the stormwater discharge and stay below state mandated threshold (i.e. Copper, lead, zinc, etc.). The FAA standard specification allows for a galvanized steel step which erodes over time and increases the amount of heavy metals at discharge points in the storm drainage system. The polypropylene plastic step described in Section 10 is a standard detail used by the City of Portland throughout the jurisdiction. This step will not erode in the stormwater and therefore allows the Port of Portland to meet the MS4 permit obligations with DEQ. |  |  |  |
| 4. DISCUSS VIABLE ALTERNATIVES (FAA ORDER 5300.1E): The standard specification allows for both galvanized steel and cast iron. We would still allow the cast iron option because iron is not currently one of the heavy metals being monitored at the outfall locations. However, the proposed polypropylene plastic is the standard, required step for manholes by the City of Portland for the area. |  |  |  |
| 5. EXPLAIN WHY MODIIFICAITON IS NECESSARY TO CONFORM TO LOCAL LAWS AND REGULATIONS (IF NECESSARY): |  |  |  |
| 6. STATE WHY MODIFICATION WOULD PROVIDE ACCEPTABLE LEVEL OF SAFETY, ECONOMY, DURABILITY, AND WORKMANSHIP (FAA ORDER 5300.1E): The City of Portland has required the use of this polypropylene plastic step because it does not erode and therefore does not introduce another source of heavy metals into the storm system. This step provides the same strength and improved durability over the galvanized steel option. This step is readily available due to being the local requirement for the Portland area and is expected to cost less than the galvanized steel option. |  |  |  |
| 7. EXPLAIN ANY SPECIAL OPERATIONAL PROCEDURES AND/OR RESTRICTIONS NECESSARY TO ACCOMMODATE MODIFICATION OF STANDARD: |  |  |  |
| INCLUDE COPY OF DOCUMENT BEING MODIFIED IN TRACK CHANGE MODE ## ATTACH ADDITIONAL SHEETS AS NECESSARY – INCLUDE SKETCH/PLAN |  |  |  |